## Structure
Summary structure
Energy & savings analysis |  |  |  | Report energy |  |  | Report safety | [5 empty] | Report maintenance | [5 empty] | Report others
Insulation | [10 empty] | Safety | [5 empty] | Maintenance | [5 empty] | Custom report
Non - insulated |  |  |  | Insulated |  |  |  | Cold |  |  | Hot Surface | Fire Protect. |  | Traffic | Housekeeping | Others | Damaged | Leakage | Condensation | Structural | Mechanical | Electrical | basic report
Surface & unknown | Pipe | Valve | Flanges | Insulated Surface & unknown | Insulated Pipe | Damaged |  | Energy | Damaged | Condensation |  | basic report |  | basic report | basic report | basic report |  |  |  | basic report | basic report | basic report
energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis |  |  | energy |  |  | energy | Report Safety |  | Report safety | Report safety | Report safety | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance

## Summary v2
| PROJECT: | Date
|  | Energy analysis |  |  |  |  | Safety |  | Maintenance | Others | TBi | Input
Component / Location |  | Energy Loss per year |  | Potential savings per year | [6 empty] | Insulation Advise | Insulated | Surface temp | Dimension | Items number
Dimension
1.- | Tank roof 58 | 868928.5868 | kWh | 690760.1095 | 827283.1169 | kWh | Railing |  | Corroded |  | Recommended | Y | 60 | 216 m²
|  | 43446.4293 | € | 34538.0055 | 41364.1558 | €
2.- | Flange 234/240 | 27663.3398 | kWh | 23111.769 | 26380.9968 | kWh | Hot Surface |  | Leakage |  | Recommended | N | 120 | DN200 | 6
|  | 1383.167 | € | 1155.5885 | 1319.0498 | €
3.- | Valve 20456 | 28012.4736 | kWh | 25399.4036 | 27136.5362 | kWh | Hot Surface |  |  |  | Recommended | N | 120 | DN200 | 0
|  | 1400.6237 | € | 1269.9702 | 1356.8268 | €
4.- | Manhole 71 | 1750.7283 | kWh/m² | 1180.0043 | 1558.2779 | kWh/m² | Hot Surface |  |  |  | Surface to be defined | N | 120 | DN200
|  | 87.5364 | €/m² | 59.0002 | 77.9139 | €/m² | Housekeeping
| Energy loss per year |  |  |  | 924604.4002 | kWh |  | Potential Energy saving per year |  |  |  | 739271.2821 |  |  | 880800.6499 | kWh
| Money loss per year |  |  |  | 46230.22 | € |  | Potential money saving per year |  |  |  | 36963.5641 |  |  | 44040.0325 | €

## Summary
| PROJECT: |  |  |  |  | Date |  |  |  | Energy price
|  | Input >>> |  |  |  | Energy analysis | [6 empty] | Safety | Maintenance | Others | Input >>>
Component / Location |  | Surface temp | Dimension | Length (m) | Items number | Heat Loss | Potential savings | [9 empty] | Operational time in hr | Medium Temp | Surface in m² |  | Number | Length or Leq | Emissivity | Ambient Temp | Surfarce Temp
|  |  | Dimension |  |  |  | from | to |  | Insulated | TBi | [8 empty] | DN
1 | Burner L6 | 56°C | 20 m² |  |  | 162897.3877 | 125881.5576 | 147129.3877 | kWh | YES | By increasing performance or thickness |  | Hot Surface | Leakage | No space
[6 empty] | 8144.8694 | 6294.0779 | 7356.4694 | € |  |  |  | Housekeeping | Electrical | Blocked
2 | Flange 2345 |  | DN200 |  | 6 | 27663.3398 | 23111.769 | 26380.9968 | kWh | NO | Recommended |  | Hot Surface | Leakage
[6 empty] | 1383.167 | 1155.5885 | 1319.0498 | €
3 | Valve 20456 |  | DN200 |  | 1 | 28012.4736 | 25399.4036 | 27136.5362 | kWh | NO | Recommended |  | Hot Surface
[6 empty] | 1400.6237 | 1269.9702 | 1356.8268 | €
4 | Pipe 2119 |  | DN200 | 10 |  | 1750.7283 | 1180.0043 | 1558.2779 | kWh | NO | Ok
[6 empty] | 87.5364 | 59.0002 | 77.9139 | €
5 | Tank roof 21 | [11 empty] | Traffic >>>
6 | Pump 234 | [12 empty] | Mechanical >>>
| Total energy loss | [6 empty] | kWh/a |  | or | #REF! | €/a
| Total potential savings | [6 empty] | kWh/a |  | or | 57829.6015
Tbi advise
TIPCHECK engineer list
List for Insulation job

## TBi
Upload documents plotplan, PFS, control room, tech specsetc…
insert some general documentation, dimension tables, flanges, etc…
PROJECT | IPCOM | DATE | 2018-05-03
USER | Luis Lopez Brunner | ENERGY PRICE | 0.05 | €/kWh
DAMAGE INSULATION

## Project
Project name
| Energy price |  | €/kWh
| Project leader |  |  |  | email
| Energy Manager |  |  |  | email
| Maintenance Manager |  |  |  | email
| HSE Manager |  |  |  | email
Upload documents plotplan, PFS, control room, tech specsetc…
insert some general documentation, dimension tables, flanges, etc…
PROJECT |  | IPCOM |  | DATE |  | 2018-05-03
USER |  | Luis Lopez Brunner |  | ENERGY PRICE |  | 0.05 | €/kWh
DAMAGE INSULATION

## Intro
Insulation report | Safety report
Maintenance report | Custom report
DAMAGE INSULATION

## Selection
SURFACES | PIPES | FLANGES | VALVES | UNDEFINED
SURFACES | PIPES | UNDEFINED |  | DAMAGED
ENERGY | CONDENSATION | DAMAGED
DAMAGE INSULATION

## Safety report
Hot surface | Fire protection | Housekeeping
Traffic | any other safety issue
DAMAGE INSULATION

## Maintenance report
Damaged insulation /cladding | Structural | Ice blocks & wet surfaces
Leakage | Mechanical equipement | Electrical equipement
DAMAGE INSULATION

## basic report
Component / Location |  | tank roof 21
hvuyfutcubjbouihoubnonojb
DAMAGE INSULATION
basic report
End

## Surface
remove medium temp
Up to ten pictures
|  | Component / Location |  |  |  | tank roof |  |  |  | Operational time |  |  | 7000 hours |  | 7000 |  |  |  | Making points & temperatures |  | add medium or surface temp
report (record ) and move to selection
|  | Surface |  |  | 216 |  | m2
[12 empty] | Heat loss |  | 868928.5868 |  | kWh/a
[14 empty] | 43446.4293 |  | €/a
|  | Surface Material |  |  | Corroded |  | 0.8
[12 empty] | Saving potential |  | 690760.1095 | 827283.1169 | kWh/a
[14 empty] | 34538.0055 | 41364.1558 | €/a
|  | Ambient Temp. |  |  | 11 |  | °C
|  | Medium or Surf Temp. |  |  | 60 |  | °C |  |  |  |  | Insulation recommended
See the different making point temperatures, or introduce themif there is no picture. Calcualte the average for calculations. Free input if there is no info
p1
|  | p2 |  |  |  | up to 10 |  | average of all the points recorded or open cell to write any value
p3
P4
Window help to calculate surfaces
a |  |  | Ø |  | Ø | *
b |  | or |  | or | h
h
*only wall
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | S Surface in m² |  | θse Medium/Surface temp | θa Amb temp | ε surface material | OT Op Time in hr | € Energy price €/kWh | hr | hcv | hse | q W/m2 | Q kWh | Q € | Savings
tank roof |  | 216 |  | 60 | 11 | 0.8 | 7000 | 0.05 | 5.3611 | 6.3672 | 11.7283 | 574.6882 | 868928.5868 | 43446.4293 | kWh | €
ref min |  | 216 |  | 60 | 11 | 0.8 | 7000 | 0.05 | 5.3611 | 6.3672 | 11.7283 | 117.8363 | 178168.4774 | 8908.4239 | 690760.1095 | 34538.0055
ref max |  | 216 |  | 60 | 11 | 0.8 | 7000 | 0.05 | 5.3611 | 6.3672 | 11.7283 | 27.5433 | 41645.4699 | 2082.2735 | 827283.1169 | 41364.1558
|  |  |  | MIN | max | [6 empty] | q W/m2
|  | θm |  | 53 | 45.5
|  | λm |  | 0.040335 | 0.03936 | [14 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses
|  | λdes |  | 0.060502 | 0.05904
|  | Insulation thickness, e |  | 0.02 | 0.1 | m
|  | Rse |  | 0.085264 | 0.085264 | value at higher temperature, conservative calculation | [5 empty] | Insulation recommended
|  | Rins |  | 0.33057 | 1.6938
|  | q ref-pb |  | 528.9739 | max heat loss for a payback of predifined Cpb | max heat loss for a payback of predifined Cpb
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte, σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
| Cpb valve and flanges |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | Cpb=investment/payback
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
Assumptions
•Measured temperature is always lower than medium temperature – conservative
•Wind speed = 0 m/s – conservative
•Up to 300 °C
•Always turbulent - H^3Δθ>10
•Energy saving calculations based on only 20 mm or 50 mm insulation depending on Δθ, (internal number not known by the user). Two options:
§Lambda simulation (Ftot=1,5) and approximated calculation q | [10 empty] | Mineral wool 1.6.2b Pipe sections 50-80 kg/m³
(hse = un-ins hse - conservative),
§Fixed values based on calculations (surfaces emissivity 0,5)
• Δθ < 25°C (20mm) - 75 % HL saving
•25°C < Δθ < 100°C (20mm)- 80 % HL saving
•100°C < Δθ (50mm) - 90 % HL saving
•Recommendation – safety first , two options
• based on payback calculation 5years and 80 €/m2 (internal number not known by the user)
•Fixed values depending on Δθ
Component |  | S Surface in m² |  | θse Medium/Surface temp | θa Amb temp | ε surface material | OT Op Time in hr | € Energy price €/kWh | hr | hcv | hse | q W/m2 | Q kWh | Q € | Savings
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref min | [8 empty] | 1 | 2 | 3 | 20 | 5 | 6 | 26 | 28
ref max | [8 empty] | 1 | 2 | 3 | 21 | 5 | 6 | 27 | 29
|  |  |  | MIN | max |  |  |  | 4: q W/m2
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14 | m
|  | Rse |  | 15 | 16 | value at higher temperature, conservative calculation |  |  | 4: 30
|  | Rins |  | 17 | 18 | bar: 4 to 6
|  | q ref-pb |  | 19 | max heat loss for a payback of predifined Cpb | max heat loss for a payback of predifined Cpb | bar: 4 to 6
DAMAGE INSULATION
DAMAGE INSULATION
Un insulated Surface
Comments
Space issue
Operational risk
Safety risk
End
New
TIPCHECK

## Pipe
|  | Component / Location |  |  | Burner /L6 | Pipe 2119 |  |  |  | Operational time |  |  | 3000 hours |  | 3000
|  | Nominal Diameter (DN) | 200 |  |  | Length |  | 10 |  | m
[12 empty] | Heat loss |  | 1750.7283 |  | kWh/a
[14 empty] | 87.5364 |  | €/a
|  | Surface Material |  |  | Metallic |  | 0.6
[12 empty] | Saving potential |  | 1180.0043 | 1558.2779 | kWh/a
[14 empty] | 59.0002 | 77.9139 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Medium or Surf Temp. |  |  | 32 |  | °C |  |  |  |  | System_ok
Component |  | DN | De (m) | Length (m) |  | θse Medium or Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
Pipe 2119 |  | 200 | 0.22 | 10 |  | 32 | 20 | 0.6 | 3000 | 0.05 | 3.6392 | 0.12778 | 3.397 | 2.7474 | 7.0363 | 0.20563 | 58.3576 | 1750.7283 | 87.5364 | kWh | €
ref min |  |  | 0.26 | 10 |  | 32 | 20 | 0.6 | 3000 | 0.05 | 3.6392 | 0.21091 | 3.2581 | 2.7474 | 6.8973 | 0.1775 | 19.0241 | 570.724 | 28.5362 | 1180.0043 | 59.0002
ref max |  |  | 0.42 | 10 |  | 32 | 20 | 0.6 | 3000 | 0.05 | 3.6392 | 0.88906 | 2.89 | 2.7474 | 6.5292 | 0.11608 | 6.415 | 192.4504 | 9.6225 | 1558.2779 | 77.9139
|  |  |  | min | max | [11 empty] | q W/m
|  | θm |  | 43.5 | 36
|  | λm |  | 0.039104 | 0.039104 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.058656 | 0.058656
|  | Insulation thickness, e |  | 0.02 | 0.1 | m
|  | D e,min/max | Dins | 0.26 | 0.42 | m
|  | Rins |  | 0.45328 | 1.7545 | [8 empty] | System_ok
|  | ql ref-pb |  | -28.7694 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 0.81682
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to communicate less
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Medium or Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql3 W/m | Q kWh | Q € | Savings
|  |  | default | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6 | kWh | €
ref min |  |  | 36 | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 44 | 6 | 26 | 28
ref max |  |  | 37 | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 44 | 6 | 27 | 29
|  |  |  | min | max | [11 empty] | q W/m
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14 | m
|  | D e,min/max | Dins | 36 | 37 | m
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 41 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Un-insulated pipe
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK
back

## Flange
|  | Component / Location |  |  | Burner /L6 | Flange 2345 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
Bottom
0,5 is the deafault value
It opens a window where Equivalent length can be modify
Equivlent length decription: Default value for flanges 0,5 m Free input - xxxxx m
|  | Nominal Diameter (DN) | 200 |  |  | Items number |  | 6 | 0.5
[12 empty] | Heat loss |  | 27663.3398 |  | kWh/a
[14 empty] | 1383.167 |  | €/a
|  | Surface Material |  |  | Corroded |  | 0.8
[12 empty] | Saving potential |  | 23111.769 | 26380.9968 | kWh/a
[14 empty] | 1155.5885 | 1319.0498 | €/a
|  | Ambient Temp. |  |  | 11 |  | °C
|  | Medium or Surf Temp. |  |  | 125 |  | °C |  |  |  |  | Insulation recommended
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
0 |  | 200 | 0.22 | 0.5 |  | 125 | 11 | 0.8 | 8760 | 0.05 | 6 | 7.3959 | 1.2139 | 5.9639 | 5.7752 | 13.3598 | 0.1083 | 1052.6385 | 27663.3398 | 1383.167 | kWh | €
ref |  |  | 0.28 | 0.5 |  | 125 | 11 | 0.8 | 8760 | 0.05 | 6 | 7.3959 | 2.5025 | 5.615 | 5.7752 | 13.0109 | 0.087374 | 173.1952 | 4551.5708 | 227.5785 | 23111.769 | 1155.5885
ref max |  |  | 0.58 | 0.5 |  | 125 | 11 | 0.8 | 8760 | 0.05 | 6 | 7.3959 | 22.2428 | 4.6804 | 5.7752 | 13.1711 | 0.041668 | 48.7954 | 1282.343 | 64.1172 | 26380.9968 | 1319.0498
|  |  |  | min | max
|  | θm |  | 85.5 | 78
|  | λm |  | 0.044825 | 0.044825 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.067238 | 0.067238
|  | Insulation thickness, e |  | 0.03 | 0.18
|  | D e,min/max | Dins | 0.28 | 0.58
|  | Rins |  | 0.57084 | 2.2946 | [8 empty] | Insulation recommended
|  | ql ref-pb |  | 952.2221 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 0.87965
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to communicate less
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
|  |  | default | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 47 | 6 | kWh | €
ref min |  |  | De,min | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 47 | 6 | 26 | 28
ref max |  |  | De,max | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 47 | 6 | 27 | 29
|  |  |  | min | max
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14
|  | D e,min/max | Dins | 36 | 37
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 48 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Un-insulated flange
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK
back

## Valve
|  | Component / Location |  |  | Burner /L6 | Valve 20456 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
Bottom
1 is the deafault value
It opens a window where Equivalent length can be modify
Equivlent length decription: Default value for valves 1 m Free input - xxxxx m
|  | Nominal Diameter (DN) | 200 |  |  | Number of items |  | 1 | 1
[12 empty] | Heat loss |  | 28012.4736 |  | kWh/a
[14 empty] | 1400.6237 |  | €/a
|  | Surface Material |  |  | Painted ε=0,8 |  | 0.8
[12 empty] | Saving potential |  | 25399.4036 | 27136.5362 | kWh/a
[14 empty] | 1269.9702 | 1356.8268 | €/a
|  | Ambient Temp. |  |  | 25 |  | °C
|  | Medium or Surf Temp. |  |  | 250 |  | °C |  |  |  |  | SAFETY-Insulation recommended
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
0 |  | 200 | 0.22 | 1 |  | 250 | 25 | 0.8 | 8760 | 0.05 | 1 | 13.4944 | 2.3958 | 7.0689 | 7.2278 | 20.5632 | 0.070362 | 3197.771 | 28012.4736 | 1400.6237 | kWh | €
ref min |  |  | 0.32 | 1 |  | 250 | 25 | 0.8 | 8760 | 0.05 | 1 | 13.4944 | 7.3728 | 6.4368 | 7.2278 | 19.9311 | 0.049908 | 298.2957 | 2613.07 | 130.6535 | 25399.4036 | 1269.9702
ref max |  |  | 0.72 | 1 |  | 250 | 25 | 0.8 | 8760 | 0.05 | 1 | 13.4944 | 83.9808 | 5.2556 | 7.2278 | 20.7221 | 0.021334 | 99.9928 | 875.9374 | 43.7969 | 27136.5362 | 1356.8268
|  |  |  | min | max
|  | θm |  | 155 | 147.5
|  | λm |  | 0.056441 | 0.056441 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thickness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.084662 | 0.084662
|  | Insulation thickness |  | 0.05 | 0.25 | m
|  | D ins | Dins | 0.32 | 0.72 | m
|  | Rins |  | 0.70438 | 2.2288 | [8 empty] | SAFETY-Insulation recommended
|  | ql ref-pb |  | 3083.0093
|  | m2/m |  | 1.0053
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to hide price calcualtion backwards
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
|  |  | default | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 47 | 6 | kWh | €
ref min |  |  | De,min | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 47 | 6 | 26 | 28
ref max |  |  | De,max | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 47 | 6 | 27 | 29
|  |  |  | min | max
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14
|  | D e,min/max | Dins | 36 | 37
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 48 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
back
Un-insulated valve
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK

## Unknow surface
|  | Component / Location |  |  | Connexion tank21 |  |  |  |  | Operational time |  |  | 6000 hours |  | 6000
1
[12 empty] | Heat loss |  | 3812.9247 |  | kWh/m²a |  |  |  | Same formulas than surface but with 1m2 by default
[14 empty] | 190.6462 |  | €/m²a
|  | Surface Material |  |  | Painted |  | 0.9
[12 empty] | Minimun Saving potential |  | 3104.6805 |  | kWh/m²a
[14 empty] | 155.234 |  | €/m²a
|  | Ambient Temp. |  |  | 15 |  | °C
|  | Medium or Surf Temp. |  |  | 65 |  | °C |  |  |  |  | Potential savings per m² if insulated. Total surface must be defined
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings |  |  |  |  | Same formulas than surface but with 1m2 by default . Only min potential savings
Connexion tank21 |  | 1 | 0 | 65 | 15 | 0.9 | 6000 | 0.05 | 6.2995 | 6.4102 | 12.7097 | 635.4874 | 3812.9247 | 190.6462 | kWh | €
ref min |  | 1 | 0 | 65 | 15 | 0.9 | 6000 | 0.05 | 6.2995 | 6.4102 | 12.7097 | 118.0407 | 708.2442 | 35.4122 | 3104.6805 | 155.234
q W/m2
|  | θm |  | 40
|  | λm |  | 0.038658 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses
|  | λdes |  | 0.057987
|  | Insulation thickness |  | 0.02 | m
|  | Rse |  | 0.07868 | value at higher temperature, conservative calculation | [6 empty] | Potential savings per m² if insulated. Total surface must be defined
|  | Rins |  | 0.3449 | [13 empty] | or | Insualtion will reduce the energy comsuption. A further analysis is needed to determine the total potential
|  | q ref-pb |  | 582.1541 | max heat loss for a payback of predifined Cpb | [13 empty] | Install insulation on surfaces at "medium temperature" °C leads to important energy savings
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
| Cpb valve and flanges |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | Cpb=investment/payback
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
Assumptions
Considering as a flat surface, conservative calculation for uninsulated and insulated
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
min | [8 empty] | 1 | 2 | 3 | 20 | 5 | 6 | 26 | 28
q W/m2
|  | θm |  | 7
|  | λm |  | 9
|  | λdes |  | 11
|  | Insulation thickness |  | 13 | m
|  | Rse |  | 15 | value at higher temperature, conservative calculation |  |  |  | 4: 31
|  | Rins |  | 17 | [13 empty] | or | Insualtion will reduce the energy comsuption. A further analysis is needed to determine the total potential
|  | q ref-pb |  | 19 | max heat loss for a payback of predifined Cpb | [13 empty] | Install insulation on surfaces at "medium temperature" °C leads to important energy savings
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
DAMAGE INSULATION
DAMAGE INSULATION
Un insulated Other
End
CHECK
back
Description

## I Surface
|  | Component / Location |  |  | Burner /L6 | Burner L6 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 400 |  | °C
|  | Surface |  |  | 20 |  | m2
[12 empty] | Heat loss |  | 162897.3877 |  | kWh/a
[14 empty] | 8144.8694 |  | €/a
|  | Surface Material |  |  | Metallic |  | 0.6
[12 empty] | Saving potential |  | 125881.5576 | 147129.3877 | kWh/a
[14 empty] | 6294.0779 | 7356.4694 | €/a
|  | Ambient Temp. |  |  | 12 |  | °C
|  | Surface Temp. |  |  | 89 |  | °C |  |  |  |  | "Savings can be achieved by increasing insulation performance or thickness"
[13 empty] | q3*op_time*surface | q3*op_time*surf*€ | saving |  | NOT TBi. Eiif table
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € |  |  | Insulation need in m
Burner L6 |  | 20 | 400 | 89 | 12 | 0.6 | 8760 | 0.05 | 4.6725 | 7.4025 | 12.0751 | 929.7796 | 162897.3877 | 8144.8694 |  |  | 0.033449
ref | min | 20 | 400 | 55 | 35 | 0.8 | 8760 | 0.05 | 5.8408 | 4.7231 | 10.5639 | 211.2776 | 37015.8301 | 1850.7915 |  |  | 0.16329
ref | max | 20 | 400 | 35 | 0.8 | 90 | 8760 | 0.05 |  |  |  | 90 | 15768 | 788.4 | kWh | € | 0.40556
[15 empty] | 125881.5576 | 6294.0779
[15 empty] | 147129.3877 | 7356.4694 | 0.1
W/mK
"Savings can be achieved by increasing insulation performance or thickness"
Default values for calcualtions | [17 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
ε ref = |  |  | 0.8
Max heat loss ref |  |  | 90 | W/M2
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q W/m2 | Q kWh | Q €
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref | min |  |  | default | default |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 26 | 28
ref | max | [10 empty] | default | 5 | 6 | 27 | 29
49
DAMAGE INSULATION
DAMAGE INSULATION
Insulated Surface
End
Comments
Space issue
Operational risk
Safety risk
TIPCHECK
back

## I Pipe
|  | Component / Location |  |  | Burner /L6 | Pipe preheater-burner |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 400 |  | °C
|  | External Diameter | 200 |  | mm | Length |  | 1 |  | m
[12 empty] | Heat loss |  | 1365.3705 |  | kWh/a
[14 empty] | 68.2685 |  | €/a
|  | Surface Material |  |  | Painted |  | 0.9
[12 empty] | Saving potential |  | 190.7306 | 366.9266 | kWh/a
[14 empty] | 9.5365 | 18.3463 | €/a
|  | Ambient Temp. |  |  | 12 |  | °C
|  | Surface Temp. |  |  | 36 |  | °C |  |  |  |  | "Savings can be achieved by increasing the insulant performance or thickness"
[17 empty] | q=(θse-θa)/Rle |  |  | saving |  | NOT Tbi. Eiif table
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q € |  |  | Rl | Insulation need in m | Di
Pipe preheater-burner |  | 200 | 0.22 | 1 | 400 | 36 | 12 | 0.9 | 8760 | 0.05 | 5.3566 | 0.25555 | 4.0398 | 3.4535 | 9.3964 | 0.15398 | 155.8642 | 1365.3705 | 68.2685 |  |  | 2.3354 | 0.086602 | 0.046797
ref min |  |  | 0.22 | 1 | 400 | 55 | 35 | 0.8 | 8760 | 0.05 | 5.8408 | 0.21296 | 3.8598 | 3.2518 | 9.7006 | 0.14915 | 134.0913 | 1174.6399 | 58.732 |  |  | 2.5729 | 0.10535
ref max |  |  | 0.22 | 1 | 400 | 55 | 35 | [9 empty] | 113.9776 | 998.4439 | 49.9222 | kWh | € | 3.0269 | 0.15056
[10 empty] | reference increasing thickness |  |  | 3.5146 | 3.2518 | 9.7006 | 0.10254 | 195.0419 |  |  | 190.7306 | 9.5365
[20 empty] | 366.9266 | 18.3463
[12 empty] | "Savings can be achieved by increasing the insulant performance or thickness" | [9 empty] | Conductivity
[22 empty] | Ft | 1.5
[22 empty] | a | 0.0338
[22 empty] | b | 0.0001173
Default values for calcualtions | [21 empty] | c | 7.545e-08
π |  |  | 3.1416 | [18 empty] | d | 7.109e-10
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
[22 empty] | 218 | 0.070322 | 0.10548
0.10548
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
Default value for ε = |  |  | 0.8
Ref max heat loss = |  |  | 85%
Increase thickness for Rls ref = |  |  | 0.05
Assumptions
For pipes system we calculate increasing performance of the insualtion system. | [8 empty] | For Rle ref , same De as component. If increaase insulation thickness , Rle will be lower and have more losses
DN | m
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q €
[11 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref min | [5 empty] | default | default |  |  |  | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref max | [10 empty] | 1 | 32 | 33 | 34 | 35 | 42 | default | 44 | 6 | kWh | €
[20 empty] | 26 | 28
[20 empty] | 27 | 29
49
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
back
TIPCHECK

## Insulated Unknown surface
|  | Component / Location |  |  | Burner /L6 | N90323 |  |  |  | Operational time |  |  | 6000 hours |  | 6000
[10 empty] | Medium Temp. |  |  | 600 |  | °C
1
[12 empty] | Heat loss |  | 1772.9872 |  | kWh/m²/a
[14 empty] | 88.6494 |  | €/m²/a
|  | Surface Material |  |  | Painted |  | 0.9
[12 empty] | Minimun Saving potential |  | 505.3218 |  | kWh/m²/a
[14 empty] | 25.2661 |  | €/m²/a
|  | Ambient Temp. |  |  | 26 |  | °C
|  | Surface Temp. |  |  | 52 |  | °C |  |  |  |  | "Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined"
[13 empty] | q3*op_time*surface | q3*op_time*surf*€ | saving |  | NOT Tbi. Eiif table
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € |  |  | Insulation need in m
N90323 |  | 1 | 600 | 52 | 26 | 0.9 | 6000 | 0.05 | 6.2106 | 5.1547 | 11.3653 | 295.4979 | 1772.9872 | 88.6494 |  |  | 0.18545
ref | N90323 | 1 | 600 | 55 | 35 | 0.8 | 6000 | 0.05 | 5.8408 | 4.7231 | 10.5639 | 211.2776 | 1267.6654 | 63.3833 |  |  | 0.25795
[15 empty] | kWh | € | 0.1
[15 empty] | 505.3218 | 25.2661 | W/mK
"Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined"
Default values for calcualtions | [17 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
θse-θa for insulation recommendation | recommendation θse-θa |  | 25 | °C
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
ε ref = |  |  | 0.8
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q €
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref min |  |  |  | default | default |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 26 | 28
Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined
DAMAGE INSULATION
DAMAGE INSULATION
Insulated Surface
End
Comments
Space issue
Operational risk
Safety risk
CHECK
back
Description

## Damaged
Component / Location |  |  | Burner /L6 | pipe preheater- burner |  |  |  | Operational time |  | 7000 hours | 7000
[8 empty] | Medium Temp. |  | 580 | °C
optional data, chack can be done with empty cells
Main dimension |  |  |  | m2 or | Øe | 500 | L | 27 | #N/A
#N/A
Surface Material |  |  | Painted ε=0,8 |  | #N/A
Cladding |  |  | Insulation
Lack of cladding |  |  | Lack of insualtion | [8 empty] | dinamic with the selection criteria yes/no
Foot traffic/Dent |  |  | Wet insulation
Highly corroded |  |  | Old insualtion
#N/A
Others |  |  | Others
Cladding
General Stament |  | --> Among others fonctions, jacketing is used to ensure the performance of the insualtion and to hold it in place.
Lack of cladding |  | --> The insulation is not protected anymore, water or other agent could get in
Foot trafic |  | --> There is a reduction of the insulation thickness, higher energy conmsuption. The system is not watertight anhmore
Highy corroded |  | --> Probably, there is a leak above in the system. Jacketing as a protecting layer gets weaker.
https://insulation.org/io/articles/maintain-insulation-jacketing-to-ensure-mechanical-insulation-performance/
Insulation
| General Stament |  | --> Any damage in the insulant leads to reduce its thermal performance and to increase the energy consumption
| Lack of insulation |  | --> A lack of insulation in a system means an easy way out/in for the heat increasing the energy consumption
| Wet insulation |  | --> Moisture inside the insulation structure can reduce the thermal performance up to 50% and increase the risk of CUI
| Old insulation |  | --> Heat cycles and external condition changes affect the estructure of the insulant reducing its performance
DAMAGE INSULATION
DAMAGE INSULATION
Damaged Insulation Cladding
End
CHECK
back
Others
Safety
Energy

## Energy
|  | SURFACES |  |  | PIPES |  |  | FLANGES |  |  | VALVES |  |  | UNDEFINED
|  | SURFACES |  |  | PIPES |  |  | UNDEFINED
1.Heat gain instead of Heat loss
2 Add risk of condensation on the surface (maintenance report)
3 No potential saving information for insulated systems
For insulated systems, general statement: any failure in the insulated system can lead to condensations and increase of energy consumption
|  | Component / Location |  |  | Burner /L6 | hikhjkl |  |  |  | Operational time |  |  | 5000 hours |  | 5000
[10 empty] | Medium Temp. |  |  | 19 |  | °C
If there is no info about medium, take surface by default
|  | Surface |  |  | 100 |  | m2
|  | Surface Material |  |  | Corroded ε=0,8 |  | #N/A
[14 empty] | #N/A |  | #N/A
[14 empty] | #N/A |  | #N/A
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 19 |  | °C |  |  |  |  | 0
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings |  |  |  |  | hr | hcv turbulent | hse | q3 W/m2
hikhjkl |  | 100 | 19 | 19 | 20 | #N/A | 5000 | 0.05 | #N/A | 1.74 | #N/A | #N/A | #N/A | #N/A | kWh | € |  |  |  | 4.5876 | 1.74 | 6.3276 | 6.3276
ref |  | 100 | 19 | 19 | 20 | #N/A | 5000 | 0.05 | #N/A | 1.74 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 4.5876 | 1.74 | 6.3276 | 1.7167
q W/m2
|  | θm |  | 19.5
|  | λm |  | 0.036121
|  | λdes |  | 0.046958
|  | Insulation thickness |  | 0.02 | m
|  | Rse |  | #N/A | value at higher temperature, conservative calculation | [6 empty] | #N/A
|  | Rins |  | 0.42592
|  | q ref-pb |  | #N/A | max heat loss for a payback of predifined Cpb
Default values for calcualtions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.3 |  |  | C | mm
| a | 0.0338 |  | Δθ < | 80 | 20
| b | 0.0001173 |  | Δθ < | 150 | 50
| c | 7.545e-08 |  | Δθ < | 250 | 80
| d | 7.109e-10 |  | Δθ < |  | 100
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 150 | €/unit
| Cpb valve and flanges |  | 3 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6
[14 empty] | Coef for payback fitting - Cpbf |  |  | 3
DAMAGE INSULATION
Un insulated Surface
Comments
Space issue
Operational risk
Safety risk
End
New
CALCULATE

## Condensation
Component / Location |  | Burner /L6 | burner |  |  | Operational time |  | 7000 hours | 7000
[6 empty] | Medium Temp. |  | 90 | °C
Main dimension |  | 23 | m2 or | Øe | L |  | #N/A
#N/A
Surface Material |  | Metallic ε=0,6 |  | #N/A
Ice block |  | yes | no
Wet surface |  | yes | no
#N/A
General Stament | --> Insulation in cold systems is critical not only for energy efficiency but for safety and process requirements
Ice block | --> Ice block indicates the failure of the insulation system (or the lack of it). A part from the potential energy savings, its weight represents a risk for the installation break down.
Wet surface | --> Condensations indicates the need of a better insulation solution to bring the surface temperature above the dew point.
https://insulation.org/io/articles/maintain-insulation-jacketing-to-ensure-mechanical-insulation-performance/
DAMAGE INSULATION
DAMAGE INSULATION
Damaged Cladding
End
Comments
Space issue
Operational risk
Safety risk
CHECK
back

## Leakage
Component / Location |  | Operational time | 5000 hours | #N/A
Medium
|  | Medium Temp. | 0 | °C
Leakage -urgent to fix
DAMAGE INSULATION
Leakage
End

## Summary default values
Material Surface - emissivity ε= |  | Coeficients |  |  |  | DN | m
Text | value | Cpb surface/pipe | 1.6 |  |  | 10 | 0.018
Defaul value | 0.8 | Cpb valve and flanges | 5 |  |  | 15 | 0.022
Metallic bright | 0.3 |  |  |  |  | 20 | 0.027
Metallic | 0.6 | thickness selection |  |  |  | 25 | 0.034
Corroded | 0.8 |  | °C | min mm | max mm | 32 | 0.043
Painted | 0.9 | Δθ < | 80 | 20 | 100 | 40 | 0.049
Non metallic | 0.9 | Δθ < | 150 | 30 | 180 | 50 | 0.061
Free input | ---- | Δθ < | 250 | 50 | 250 | 60 | 0.072
|  | Δθ < |  | 80 | 300 | 65 | 0.077
Operational time | [5 empty] | 80 | 0.089
Text | value | Conductivity |  |  |  | 100 | 0.115
1000 hours | 1000 | Ft | 1.5 |  |  | 125 | 0.141
2000 hours | 2000 | a | 0.0338 |  |  | 150 | 0.169
3000 hours | 3000 | b | 0.0001173 |  |  | 200 | 0.22
4380 hours (1/2 year) | 4380 | c | 7.545e-08 |  |  | 250 | 0.273
5000 hours | 5000 | d | 7.109e-10 |  |  | 300 | 0.324
6000 hours | 6000 |  |  |  |  | 350 | 0.356
7000 hours | 7000 |  |  |  |  | 400 | 0.407
8760 hours (full year) | 8760 |  |  |  |  | 450 | 0.458
free input | [5 empty] | 500 | 0.508
[6 empty] | 600 | 0.61
[6 empty] | 700 | 0.712
Number or constants | [5 empty] | 800 | 0.813
π | 3.1416 |  |  |  |  | 900 | 0.915
Boltzmann cte σ= | 5.6704e-08 |  |  |  |  | 1000 | 1.016
Safety warning for θse> | 55 |  |  |  |  | 1100 | 1.12
Criteria for Insulated, θse ref | 55 |  |  |  |  | 1200 | 1.22
Criteria for Insulated, θa ref | 35 |  |  |  |  | 1400 | 1.42
ε ref = | 0.8 |  |  |  |  | 1500 | 1.52
Max heat loss ref | 90 |  |  |  |  | 1600 | 1.62
Criteria for Insulated, Ref max heat loss = | 0.85 |  |  |  |  | 1800 | 1.82
Safety warning for cold θse< | 0 |  |  |  |  | 2000 | 2.02
[6 empty] | 2000 | 2.02
[6 empty] | 2200 | 2.22
[6 empty] | 2400 | 2.42
[6 empty] | 2600 | 2.62
[6 empty] | 2800 | 2.82
[6 empty] | 3000 | 3.02
[6 empty] | 3200 | 3.22
[6 empty] | 3400 | 3.42

## Default values
emissivity |  | operation hours |  | Safety risk
Defaul value | 0.8 | 1000 hours | 1000 | hot surface
Metallic bright | 0.3 | 2000 hours | 2000 | fire protection
Metallic | 0.6 | 3000 hours | 3000 | leakage
Corroded | 0.8 | 4380 hours (1/2 year) | 4380 | dangerous
Painted | 0.9 | 5000 hours | 5000 | other
Non metallic | 0.9 | 6000 hours | 6000
Free input |  | 7000 hours | 7000
|  | 8760 hours (full year) | 8760
free input
Defaul value ε=0,8
Metallic bright ε=0,3
Metallic ε=0,6
Corroded ε=0,8
Painted ε=0,9
Non metallic ε=0,9
Free input

## Warning list
Criteria | Warning | Advise | Action | Surface | Pipe | Flange | Valve | Undefined | I Surface | I Pipe | I Undefined
Work flow
If component/location field is empty | Please input Component/ Location |  | no calculation | x | x | x | x | x | x | x | x
If operational time is empty | Please input operational time |  | no calculation | x | x | x | x | x | x | x | x
If surface is empty | Please input surface in m² |  | no calculation | x |  |  |  | x | x |  | x
If External Diameter (Ø) is empty | Please input external diameter (Ø) |  | no calculation | [6 empty] | x
If Length is empty | Please input length |  | no calculation |  | x |  |  |  |  | x
If Nominal Diameter (DN) is empty | Please input nominal diameter (DN) |  | no calculation |  | x | x | x
If Items number of items is empty | Please input items number |  | no calculation |  |  | x | x
If surface material is empty | Please input surface emissivity |  | no calculation | x | x | x | x | x | x | x | x
If ambient temperature is empty | Please input Ambient temperature |  | no calculation | x | x | x | x | x | x | x | x
If medium/surface temperature is empty | Please input Medium/surface temperature |  | no calculation | x | x | x | x | x
If medium temperature is empty | Please input medium temperature |  | no calculation | [5 empty] | x | x | x
If surface temperature is empty | Please input surface temperature |  | no calculation | [5 empty] | x | x | x
If surface temperature < medium temperature & < ambient temp | Please check temperatures |  | no calculation
If medium/surface temperature < safety warning for cold θse ( default value) |  | Risk of condesation/ ice | indicate Cold Surface in the summary (safety) | x | x | x | x | x
If surface temperature < safety warning for cold θse ( default value) |  | Risk of condesation / ice | indicate Cold Surface in the summary (safety) | [5 empty] | x | x | x
If surface temperature > "Safety warning for θse" default value |  | "SAFETY - Insulation required" | indicate Hot Surface in the summary (safety) | x | x | x | x | x | x | x | x
If medium temp - surface temp < 15 °C (absolute value) | It is an un-insulated system |  | no calculation | [5 empty] | x | x | x
If savings < 0 |  | System ok | no saving output | [5 empty] | x | x | x
If savings < 0 |  | System ok | no saving output | [5 empty] | x | x | x

## TBi advise
Advise in the component screen (formulas 30, 31, 49, 50) | Summary | Surface | Pipe | Flange | Valve | Undefined | I Surface | I Pipe | I Undefined
System ok | OK | x | x | x | x |  | x | x
Insulation recommended | Recommended | x | x | x | x
SAFETY - Insulation recommended | Recommended | x | x | x | x | x | x | x | x
Total surface must be defined. Units per m² | Define total surface |  |  |  |  | x |  |  | x
Saving can be achieved …….. | ↑ Performance or thickness | [5 empty] | x | x

## todo
information by selection
equivalent length
disclaimer about wind speed and sun radiation factor

## Andreas
inforamtion at the selection
DN or diameter
uninsulated others - only info per m2, no recommendation just conditional
Jacketing or cladding?
CO2 emission reduction?
Cold workflow
Limitation in temperatures, like up to 300 °C
Calculate or TIPCHECK?
Commmertialization
Bugs control with customers
round outputs ??